## Spec
Si.No | Description
1 | The Hydrogen Gas detection and alarm system shall have a catalytic bead type sensor transmittor built in
2 | The system shall have 1 inch 7 segment 3 digit display to show the persentage of Hydrogen gas in LEL. ( Low Explosive Limit)
3 | The system shall have analog output to reproduce the displayed value in 0-10V / 0 -20 mA
4 | The system shall have volt free relay output to trigger the exhaust fan in a user programmed time to exhaust the air inside room. The user shall set the cycle time and run duration of the exhaust fan
5 | Volt free output for 3rd party integration shall be avaliable.
6 | The system shall have soft integration through MODBUS RTU for BMS connectivity.

## BOQ
Technical specification for Hydrogen Gas Detection System
Si.No | Description
1 | Supply of Hydrogen gas sensor with pellister catalyst bead type with inbuilt Dsisplay. The sensor transmittor shall have the following features
a. 3 Dig 7 segment display
b. Inbuil buzzer
c. Volt free output for 3rd party integration
d. 0-10V / 0-20mA Analog output for BMS
e. Volt fee output for Exhaust fan automation with built in timer
f. RS485 port for BMS soft intgration through MODBUS RTU
2 | 24V Hooter
3 | 24V/2.1 A SMPS
4 | Starter panel to control the exhaust fan with aux contacts, terminals, wiring with all accessories complet as per requirement
5 | 2C X 1.5 Sq.mm shielded twisted cable for BMS connectivity
6 | 2C X 1.0 Sq.mm cable for Exhaust fan control
7 | 2C X 1.0 Sq.mm cable for Hooter
8 | 2C X 1.0 Sq.mm cable for 3rd party FAS / DCS integration