ADDRESSABLE

WATER LEAK DETECTION SYSTEM

1.0	Overview

A liquids leak detection system is recommended for a continuous protection from the risk of water and other liquids leakage in the building.

This complete liquids leak detection system shall be based on a digital monitoring unit, addressable sense cables, communicating cables and all required auxiliary equipment. This system shall detect and locate leaks simultaneously as well as cable break faults.

2.0	System performance

2.1	General

The liquids leak detection system shall identify any abnormal presence of liquid on any point of its connected sense cables, to the nearest metre. In the event of leakage, an audible alarm is triggered, the indicator light changes to red, the dry contact is activated and the display shows details of the fault, and its location to the nearest metre.

2.2	Sense cable length

The system shall be capable of monitoring up to 3200 meter of cable from monitoring unit. This length shall not include the communicating cable.

2.3	Multiple leaks

The system shall be capable of managing information of all leaks related to the number of sense cables installed. (E.g. 32 sense cables installed=32 possible detected and displayed leaks).

2.4	Cable break fault

Besides leak, the system shall be capable to detect circuit interruption (cable break) on any of its connected sense cables. In the event of a “cable break”, an audible alarm is triggered, the indicator light changes to red, the dry contact is activated and the display shows “cable break” and its location.

2.5	Liquid types

The system shall be capable of detecting conductive liquids, as water.  These sense cables shall be able to be connected simultaneously on one digital monitoring unit.

2.6	Security

To enter the event menu, the system shall require a password.

3.0	Products

3.1	Sense cable

3.1.1	Performance

The sense cable shall continuously perform three functions: to detect the presence of water at any point along its length, to detect a cut or break at any point along its length and to communicate digitally the nature and location of the fault to the nearest metre.

3.1.2	Construction

The sense cable shall consist of a helically-winded core, on which PEHD (Polyethylene high-density) conductor wires are spiraled. This shall ensure a prompt detection as well as a short drying time after the risk is eliminated.

The insulation and signal wire s shall be of polymer. The jacket of sense wires shall be of conductive polymer on the ground wire. The active sense wire shall have special dust-proof construction and shall not be affected if in contact with any solid particles.

3.1.3 Monitoring slave unit shall be a microcontroller based system capable of monitoring the sensor cable connected to it. A display shall provide the access to configure parameters. Also the display shall show the types of events monitored in the cable & communicate the information to the main master panel.

3.1.4 Each monitoring salve unit shall have a unique slave address to identify itself in the master panel.

3.1.5 The status of the sense cable shall be indicated by the display in the monitoring slave unit..

3.1.6 The sense cable shall be made of an abrasive-resistant material, tested in hostile environments. The sense cable shall be made of light and flexible material in an easily identifiable colour.

3.1.7 There shall be pre-finished connection accessories. Communicating cable as well as end termination plug shall bring the continuity to each circuit.

3.2	Digital monitoring unit

3.2.1	General

The digital monitoring unit shall be a microprocessor based complete leak locating system. It shall receive data processed and transmitted by the sense cables as well a s raising the alarm.

3.2.2 Power

The digital monitoring unit shall be supplied by 240 VAC, 50/60Hz, single phase.

The total power consumption shall not exceed 16 VA.

3.2.3	Buttons shall have on the front of digital monitoring unit:-

3.2.3.1

The monitoring unit shall start a self-test automatically once powered on. The name and total quantity of cables on every output shall be keyed on the LCD display of the digital monitoring unit.

3.2.3.2 “Mute”: to acknowledge and silence the alarm

3.2.3.3 “Menu”: to configure the digital monitoring unit

3.2.3.4 “History”: to record alarm history

Event log of (100) events deep shall provide storage on a FIFO basis. When the memory is full, the latest record shall be stored and the earliest record shall then drop out automatically.

3.2.4	Communication

There shall be configurable dry contacts available in the system to enable remote monitoring and control. The dry contacts shall indicate normal and alarm condition. They shall be embedded with possible extension if required.

The digital monitoring unit s hall be compatible with existing operating systems. RS-485 serial ports with Modbus/BACnet communication protocol shall be available on the digital monitoring unit, so as to interface with executive and streamline printing.

3.2.5	Enclosure

The digital monitoring unit shall be enclosed in standard metal enclosure.

3.2.6	LCD display

A four (4) lines by twenty (2 0) characters backlit LCD shall be located on the front of the digital monitoring unit. In the event of simultaneous leaks or multiple faults, the display shall show all alarms one after the other. English language shall be the language by default.

3.2.7	Indicator light

An indicator light placed at the front of the digital monitoring unit shall indicate both power and alarm status.

3.2.8	Qualifications

3.3	Jumper cable connection and auxiliary equipment

3.3.1 Where leak detection is required, a four core jumper cable shall be used to connect sense cables in between zones, floors or rooms.

3.3.2 Warning labels shall be placed on the sense cable approximately every five (5) meters. Hold-down clips shall be used to fix the sense cables every one (1) meter.

3.3.3	Floor plan

Schematic drawings shall be representing the layout of the leak detection system installed. It shall indicate the location of sense cables, jumper cables and all auxiliary equipments, as per the example below.

It shall be provided by the contractor installing the water leak detection system. The floor plan is essential for a good management of the leak detection system since it makes it possible to locate quickly the fault, as indicated by the digital monitoring unit.

4.0	Installation

The system shall be installed by well trained staff, with the procedure recommended by the manufacturer.